## 36kV Bus
Positive Sequence Impedances to 36 kV Busses | [7 empty] | Zero Sequence Impedances to 36 kV Busses
36 kV Base Voltage | [7 empty] | 36 kV Base Voltage
Station | Supplied from (System) | Transformer No. - kVA | Tap Ratio | % Z @ 100MVA | D e @ 120 V | Short Circuit MVA |  | % Zo @ 100MVA | % Z (L_G) @ 100MVA | Short Circuit MVA |  |  | Update
AN-1 & 3 | 138 | 2-100,000 | 138-37.5 | 0.31+9.75j | 0.11706 | 1025.123 | 9.7549 | 0.23+15.64j | 0.85+35.14j | 853.4783 | * | 35.1503 | 2012-03-13 | Per CAPE
AD-1 | 138 | 1-36,000 | 138-37.5 | 1.30+24.6j | 0.29561 | 405.9376 | 24.6343 | 1.11+23.3j | 3.71+72.5j | 413.2524 |  | 72.5949
DS-1 & 3 | 138 | 2-90,000 | 139-36-13.8 | 0.69+11.05j | 0.13286 | 903.2182 | 11.0715 | 0.70+16.98j | 2.08+39.08j | 766.5711 |  | 39.1353 | 2016-04-05 | Per CAPE
GW-1,3 & 4 | 138 | 3-90,000 | 135.24-36-12 | 0.27+7.47j | 0.089699 | 1337.8145 | 7.4749 | 0.25+10.87j | 0.79+25.81j | 1161.7961 |  | 25.8221 | 2016-04-05 | Per CAPE
HM-2, 3, 4 & 5 | 138 | 4-36,000 | 138.8-36-11.5 | 0.44+8.86j | 0.10645 | 1127.2789 | 8.8709 | 0.32+11.27j | 1.2+28.99j | 1033.9542 |  | 29.0148 | 2016-04-05 | Per CAPE
IV-2, 3 & 4 | 138 | 3-60,000 | 138.6-36-13.65 | 0.37+9.42j | 0.11313 | 1060.7532 | 9.4273 | 0.44+12.96j | 1.18+31.8j | 942.7474 |  | 31.8219 | 2012-09-13 | Per CAPE
JD-1, 2 & 3 | 138 | 2-52,500 | 141.45-36-13.8 | 0.36+7.42j | 0.089145 | 1346.1255 | 7.4287 | 0.38+12.44j | 1.1+27.28j | 1098.8138 |  | 27.3022 | 2016-04-05 | Per CAPE
LY-2,3 & 4 | 138 | 3-52,000 | 138.6-36-13.65 | 0.45+7.38j | 0.088724 | 1352.5016 | 7.3937 | 0.45+10.56j | 1.35+25.32j | 1183.1536 |  | 25.356 | 2017-02-27 | Per CAPE
MF-1, 2, 3 & 4 | 138 | 2-40,000 1-46,000 1-60,000 | 145.2-36-13.65 | 0.38+7.17j | 0.086161 | 1392.7455 | 7.1801 | 0.87+13.78j | 1.63+28.12j | 1065.0685 |  | 28.1672 | 2016-04-05 | Per CAPE
NF-1, 2, 3 & 4 | 138 | 3-45,000 1-44,000 | 138.6-36-13.65 | 0.37+6.82j | 0.08196 | 1464.1226 | 6.83 | 0.32+10.58j | 1.06+24.22j | 1237.4612 |  | 24.2432 | 2016-04-05 | Per CAPE
NT-2 & 3 | 138 | 2-90,000 | 138-36 | 0.45+11.11j | 0.13343 | 899.3526 | 11.1191 | 0.43+17.08j | 1.33+39.3j | 762.922 |  | 39.3225 | 2016-04-05 | Per CAPE
NY-1, 2 & 3 | 138 | 3-30,000 | 145.2-36-13.8 | 0.72+10.07j | 0.12115 | 990.52 | 10.0957 | 0.55+19.30j | 1.99+39.44j | 759.6827 |  | 39.4902 | 2016-04-05 | Per CAPE
SN-1, 3 & 4 | 138 | 3-40,000 | 138.6-36-13.2 | 0.82+11.35j | 0.13655 | 878.7669 | 11.3796 | 0.68+17.82j | 2.32+40.52j | 739.1645 |  | 40.5864 | 2016-04-07 | Per CAPE
SP-1 | 138 | 1-60,000 | 138-36-13.2 | 1.48+24.83j | 0.29849 | 402.0251 | 24.8741 | 0.82+9.96j | 3.78+59.62j | 502.1785 |  | 59.7397 | 2012-05-17 | Per CAPE
ST-1 | 138 | 1-75,000 | 138-37.5-13.2 | 2.08+18.79j | 0.22686 | 528.9669 | 18.9048 | 0.46+30.28j | 4.62+67.86j | 441.0656 |  | 68.0171 | 2016-04-07 | Per CAPE
ZN-2 | 138 | 1-30,000 | 140-36-13.2 | 2.33+33.60j | 0.40417 | 296.906 | 33.6807 | 2.75+26.59j | 7.41+93.79j | 318.8699 |  | 94.0823 | 2012-11-11 | Per CAPE

## 36kV Line
Positive Sequence 36 kV Line and Cable Impedance | [7 empty] | Zero Sequence 36 kV Line and Cable Impedance
Overhead | [7 empty] | Overhead
Wire Type | % Z+ Per Mile @ 100 MVA | [6 empty] | Wire Type | % Zo Per Mile @ 100 MVA
1192.5 MCM - Wood Pole | 0.61+4.52j | = | 4.561 | Ð | 82.314 |  | 1.4367 | 1192.5 MCM - Wood Pole | 5.15+19.42j | = | 20.0913 | Ð | 75.1476 | 1.3116
1192.5 MCM - Steel Pole | 0.63+5.36j | = | 5.3969 | Ð | 83.2964 |  | 1.4538 | 1192.5 MCM - Steel Pole | 4.62+18.27j | = | 18.8451 | Ð | 75.8089 | 1.3231
795 MCM ACSR - Wood Pole | 0.98+4.63j | = | 4.7326 | Ð | 78.049 |  | 1.3622 | 795 MCM ACSR - Wood Pole - With Ground | 5.13+20.91j | = | 21.5301 | Ð | 76.2155 | 1.3302
795 MCM ACSR - Steel Pole | 0.91+5.55j | = | 5.6241 | Ð | 80.6884 |  | 1.4083 | 795 MCM ACSR - Wood Pole - W/O Ground | 3.19+22.30j | = | 22.527 | Ð | 81.8591 | 1.4287
636 MCM ACSR | 1.14+4.54j | = | 4.6809 | Ð | 75.9044 |  | 1.3248 | 795 MCM ACSR - Steel Pole - With Ground | 4.90+18.46j | = | 19.0993 | Ð | 75.1343 | 1.3113
477 MCM ACSR | 1.64+4.84j | = | 5.1103 | Ð | 71.2814 |  | 1.2441 | 795 MCM ACSR - Steel Pole - W/O Ground | 3.12+24.04j | = | 24.2416 | Ð | 82.6053 | 1.4417
336 MCM ACSR | 2.40+4.65j | = | 5.2328 | Ð | 62.7004 |  | 1.0943 | 636 MCM ACSR - With Ground | 6.04+20.04j | = | 20.9304 | Ð | 73.2273 | 1.2781
300 MCM - 19 Strand Cu | 1.52+5.04j | = | 5.2642 | Ð | 73.2174 |  | 1.2779 | 636 MCM ACSR - W/O Ground | 3.34+23.94j | = | 24.1719 | Ð | 82.0576 | 1.4322
4/0 Cu | 2.15+5.16j | = | 5.59 | Ð | 67.3801 |  | 1.176 | 477 MCM ACSR - With Ground | 5.83+21.42j | = | 22.1992 | Ð | 74.7743 | 1.3051
4/0 ACSR | 3.42+5.84j | = | 6.7677 | Ð | 59.6461 |  | 1.041 | 477 MCM ACSR - W/O Ground | 3.84+22.82j | = | 23.1408 | Ð | 80.4481 | 1.4041
1/0 Cu | 4.29+6.05j | = | 7.4166 | Ð | 54.6599 |  | 0.954 | 336 MCM ACSR | 7.37+15.83j |  | 17.4616 |  | 65.0346 | 1.1351
1/0 - 7 Strand Al | 6.66+5.56j | = | 8.6758 | Ð | 39.8563 |  | 0.69562 | 300 MCM - 19 Strand Cu - With Ground | 6.42+20.54j | = | 21.5199 | Ð | 72.6428 | 1.2679
[8 empty] | 300 MCM - 19 Strand Cu - W/O Ground | 8.86+24.96j | = | 26.4859 | Ð | 70.4568 | 1.2297
Cable Type | % Z+ Per 1000' @ 100 MVA | [6 empty] | 4/0 Cu - With Ground | 7.05+20.66j | = | 21.8298 | Ð | 71.1584 | 1.2419
[8 empty] | 4/0 Cu - W/O Ground | 4.35+24.56j | = | 24.9423 | Ð | 79.9561 | 1.3955
350 MCM Cu 3-Conductor PILC | 0.23+0.49j | = | 0.54129 | Ð | 64.8552 |  | 1.1319 | 4/0 ACSR - With Ground | 8.32+21.34j | = | 22.9045 | Ð | 68.7003 | 1.199
1/0 Cu 3-Conductor PILC | 1.41+0.66j | = | 1.5568 | Ð | 25.0836 |  | 0.43779 | 4/0 ACSR - W/O Ground | 5.62+25.24j | = | 25.8581 | Ð | 77.4472 | 1.3517
1500 MCM Al 1-Conductor XLP | 0.20+0.48j | = | 0.52 | Ð | 67.3801 |  | 1.176 | 1/0 Cu - With Ground | 9.19+22.55j | = | 24.3507 | Ð | 67.8272 | 1.1838
750 MCM Cu 1-Conductor PIAS | 0.26+0.24j | = | 0.35384 | Ð | 42.7094 |  | 0.74542 | 1/0 Cu - W/O Ground | 6.49+25.45j | = | 26.2645 | Ð | 75.6939 | 1.3211
250 MCM Cu 1-Conductor PIAS | 0.54+0.32j | = | 0.62769 | Ð | 30.6507 |  | 0.53496 | 1/0 - 7 Strand Al - With Ground | 11.56+21.06j | = | 24.0241 | Ð | 61.2373 | 1.0688
2/0 Cu 1-Conductor PIAS | 0.90+0.39j | = | 0.98087 | Ð | 23.4287 |  | 0.40891 | 1/0 - 7 Strand Al - W/O Ground | 8.86+24.96j | = | 26.4859 | Ð | 70.4568 | 1.2297
500 MCM Cu 1-Conductor EPR | 0.21+0.44j | = | 0.48754 | Ð | 64.4861 |  | 1.1255
1000 MCM Al 1-Conductor XLP | 0.24+0.54j | = | 0.59093 | Ð | 66.0375 |  | 1.1526 | Cable Type | % Zo Per 1000' @ 100 MVA
4/0 Al 1-Conductor XLP | 0.76+0.33j | = | 0.82855 | Ð | 23.471 |  | 0.40965
[6 empty] | * |  | 350 MCM Cu 3-Conductor PILC | 2.44+0.45j | = | 2.4811 | Ð | 10.4494 | 0.18238
[8 empty] | 1500 MCM Al I-Conductor XLP | 0.51+4.91j | = | 4.9364 | Ð | 84.07 | 1.4673
[8 empty] | 750 MCM Cu 1-Conductor PIAS | 0.28+0.18j | = | 0.33287 | Ð | 32.7352 | 0.57134
[8 empty] | 250 MCM Cu 1-Conductor PIAS | 0.59+0.23j | = | 0.63325 | Ð | 21.2974 | 0.37171
[8 empty] | 2/0 Cu 1-Conductor PIAS | 0.97+0.27j | = | 1.0069 | Ð | 15.5546 | 0.27148
[6 empty] | ** |  | 500 MCM Cu 1-Conductor EPR | 2.44+0.45j | = | 2.4811 | Ð | 10.4494 | 0.18238
[6 empty] | ** |  | 1000 MCM Al 1-Conductor XLP | 2.09+0.82j | = | 2.2451 | Ð | 21.4223 | 0.37389
[6 empty] | ** |  | 4/0 Al 1-Conductor XLP | 1.15+5.58j | = | 5.6973 | Ð | 78.3548 | 1.3675
[6 empty] | * |  | Based on earth return exclusively because shield interrupts are used on this cable
[6 empty] | ** |  | Calculations do not include separate bond wire because there is no standard configuration

## 13kV Bus
Positive Sequence Impedances to 13.2 kV Busses | [7 empty] | Zero Sequence Impedances to 13.2 kV Busses
13.2 kV Base Voltage | [7 empty] | 13.2 kV Base Voltage
Station | Supplied from (System) | Transformer No. - kVA | Tap Ratio | % Z @ 100MVA | D e @ 120 V | Short Circuit MVA |  | % Zo @ 100MVA | % Z (L_G) @ 100MVA | Short Circuit MVA |  | Update
AT-1* |  | 1-45,000 |  | 0.8+22.9j | 0.27497 | 436.415 | 22.914 | 20.5+512.8j | 22.1+558.6j | 53.6637 | 559.037 | 2019-02-13
AT-2* |  | 1-45,000 |  | 0.8+22.9j | 0.27497 | 436.415 | 22.914 | 25.1+627.1j | 26.7+672.9j | 44.5481 | 673.4295 | 2019-02-13
AC-71 | AN | 1-14,000 | 36-13.2 | 12.7+89.8j | 1.0883 | 110.2614 | 90.6936 | 3.2+51.7j | 28.6+231.3j | 128.7214 | 233.0615 | 2017-04-11
AS-71 | 138 | 1-20,000 | 134.55-13.8 | 4.0+71.2j | 0.85575 | 140.2283 | 71.3123 | 3.8+69.6j | 11.8+212j | 141.2907 | 212.3281 | 2016-04-22
AS-72 | 138 | 1-20,000 | 134.55-13.8 | 3.5+73.7j | 0.8854 | 135.5325 | 73.7831 | 3.3+72.2j | 10.3+219.6j | 136.462 | 219.8414 | 2016-04-22
AG-71 | 138 | 1-11,500 | 138-13.2 | 4.3+77.3j | 0.92903 | 129.1664 | 77.4195 | 3.1+73.1j | 11.7+227.7j | 131.5787 | 228.0004 | 2016-04-19
BT-71 | 138 | 1-16,800 | 138-13.2 | 2.9+73.1j | 0.87789 | 136.6914 | 73.1575 | 2.5+67.9j | 8.3+214.1j | 140.0163 | 214.2608 | 2017-12-20
CF-71 | 138 | 1-20,000 | 134.55-13.8 | 4.5+72.7j | 0.87407 | 137.2888 | 72.8391 | 3.9+69.5j | 12.9+214.9j | 139.349 | 215.2868 | 2016-04-22
CF-72 | 138 | 1-20,000 | 134.55-13.8 | 4.5+78.4j | 0.94235 | 127.3414 | 78.529 | 3.8+73.9j | 12.8+230.7j | 129.8393 | 231.0548 | 2016-04-22
CW-71 | 138 | 1-33,600 | 138-13.8 | 2.0+52.5j | 0.63046 | 190.3381 | 52.5381 | 1.5+49.3j | 5.5+154.3j | 194.303 | 154.398 | 2016-04-22
CW-72 | 138 | 1-12,000 | 138-13.2 | 3.6+77.2j | 0.92741 | 129.3931 | 77.2839 | 3.1+73.9j | 10.3+228.3j | 131.2725 | 228.5322 | 2012-07-18
CY-71 | 138 | 1-12,000 | 138-13.8 | 4.3+71.7j | 0.86195 | 139.2199 | 71.8288 | 3.8+69.1j | 12.4+212.5j | 140.9367 | 212.8615 | 2016-03-15
DA-72 | DS | 1-20,000 | 36.2-13.8 | 7.4+89.2j | 1.0741 | 111.7238 | 89.5064 | 5.0+69.1j | 19.8+247.5j | 120.8261 | 248.2907 | 2016-04-26
DB-71 | 138 | 1-20,000 | 134.55-13.8 | 4.0+75.8j | 0.91087 | 131.7428 | 75.9055 | 3.2+69.8j | 11.2+221.4j | 135.3283 | 221.6831 | 2018-09-06
DB-72 | 138 | 1-30,000 | 134.55-13.8 | 3.7+72.2j | 0.86754 | 138.3226 | 72.2947 | 3.0+67.1j | 10.4+211.5j | 141.6728 | 211.7555 | 2018-09-06
DG-71 | DS | 1-20,000 | 36.2-13.8 | 5.4+66.3j | 0.79823 | 150.3318 | 66.5195 | 3.8+47.5j | 14.6+180.1j | 166.0295 | 180.6908 | 2016-05-03 | No Transformer Test Report used X/R from 72-IL
DK-71 | 138 | 1-20,000 | 134.55-13.8 | 4.9+76.7j | 0.92228 | 130.1129 | 76.8564 | 4.2+73.3j | 14+226.7j | 132.0819 | 227.1319 | 2018-09-13 | No Transformer Test Report used X/R from 71-IP
DL-71 | 138 | 1-20,000 | 134.55-13.8 | 4.6+76.2j | 0.91606 | 130.9951 | 76.3387 | 4.1+72.3j | 13.3+224.7j | 133.2781 | 225.0933 | 2016-08-08
DL-72 | 138 | 1-20,000 | 134.55-13.8 | 5.1+77.1j | 0.92722 | 129.4189 | 77.2685 | 4.1+72.1j | 14.3+226.3j | 132.3035 | 226.7514 | 2016-08-08
DO-72 | AN | 1-12,500 | 134.55-13.8 | 27.8+144.2j | 1.7623 | 68.0942 | 146.8553 | 3.0+65.2j | 58.6+353.6j | 83.7 | 358.4228 | 2016-08-08
DW-71 | 138 | 1-18,000 | 138-13.8 | 2.6+72.5j | 0.87056 | 137.8424 | 72.5466 | 1.9+68.3j | 7.1+213.3j | 140.5691 | 213.4181 | 2012-02-21
ED-71 | DS | 1-12,500 | 36.2-13.8 | 13.0+99.2j | 1.2006 | 99.9518 | 100.0482 | 5.4+64.9j | 31.4+263.3j | 113.1368 | 265.1657 | 2016-08-08
ED-72 | DS | 1-12,500 | 36.2-13.8 | 11.5+94.5j | 1.1424 | 105.0451 | 95.1972 | 5.3+64.4j | 28.3+253.4j | 117.6584 | 254.9754 | 2016-08-08
EG-72 | SP | 1-5,000 | 35.3-13.2 | 26.9+176.3j | 2.1401 | 56.0725 | 178.3404 | 12.3+119.6j | 66.1+472.2j | 62.9189 | 476.804 | 2018-09-06
EN-71 | 138 | 1-30,000 | 138-13.8 | 2.6+69.5j | 0.83458 | 143.7843 | 69.5486 | 2.2+66.1j | 7.4+205.1j | 146.175 | 205.2335 | 2018-09-06
EN-72 | 138 | 1-30,000 | 134.55-13.8 | 2.5+67.9j | 0.81535 | 147.1757 | 67.946 | 2.2+65.7j | 7.2+201.5j | 148.7884 | 201.6286 | 2018-09-06 | 6.01%Z per nameplate, No test report. Used 10.5 X/R
EP-71 | DS | 1-20,000 | 36.2-13.8 | 14.1+107.7j | 1.3034 | 92.0649 | 108.6191 | 5.1+67.5j | 33.3+282.9j | 105.3174 | 284.8531 | 2016-08-08
ER-71 | 138 | 1-18,000 | 138-36 | 2.5+69.8j | 0.83814 | 143.1747 | 69.8448 | 1.8+64.5j | 6.8+204.1j | 146.9053 | 204.2132 | 2014-11-18
ES-71 | 138 | 1-20,000 | 134.55-13.8 | 4.2+71.0j | 0.85349 | 140.5993 | 71.1241 | 3.9+68.9j | 12.3+210.9j | 142.0062 | 211.2584 | 2016-08-08
ES-72 | 138 | 1-20,000 | 134.55-13.8 | 4.1+73.5j | 0.88337 | 135.8432 | 73.6143 | 3.8+69.3j | 12+216.3j | 138.4833 | 216.6326 | 2016-08-08
ET-71 | 138 | 1-30,000 | 134.55-13.8 | 3.6+71.3j | 0.85669 | 140.074 | 71.3908 | 2.5+66.2j | 9.7+208.8j | 143.5234 | 209.0252 | 2016-08-11
EW-71 | DS | 1-20,000 | 33.3-13.8 | 9.7+105.5j | 1.2713 | 94.3886 | 105.945 | 4.7+68.6j | 24.1+279.6j | 106.8998 | 280.6367 | 2016-08-08
EY-71 | 138 | 1-30,000 | 134.55-13.8 | 2.5+69.5j | 0.83454 | 143.7919 | 69.5449 | 1.8+63.9j | 6.8+202.9j | 147.7731 | 203.0139 | 2016-08-11
EY-72 | 138 | 1-30,000 | 134.55-13.8 | 2.5+70.2j | 0.84293 | 142.3599 | 70.2445 | 1.8+64.6j | 6.8+205j | 146.261 | 205.1127 | 2016-08-11
FB-71 | 138 | 1-30,000 | 134.55-13.8 | 3.3+66.6j | 0.80018 | 149.9662 | 66.6817 | 3.0+64.2j | 9.6+197.4j | 151.7963 | 197.6333 | 2016-08-11
FC-71 | HM | 1-12,500 | 34.4-13.8 | 24.0+120.4j | 1.4732 | 81.454 | 122.7687 | 3.0+65.3j | 51+306.1j | 96.6745 | 310.3195 | 2016-08-11
FD-71 | DS | 1-12,000 | 34.4-13.8 | 10.7+106.3j | 1.282 | 93.6004 | 106.8372 | 3.5+65.4j | 24.9+278j | 107.4834 | 279.1129 | 2018-03-15
FU-71 | 138 | 1-30,000 | 134.55-13.8 | 2.8+64.6j | 0.77593 | 154.6536 | 64.6607 | 2.6+62.3j | 8.2+191.5j | 156.5145 | 191.6755 | 2016-04-01
GA-71 | HM | 1-20,000 | 36.2-13.8 | 13.6+98.8j | 1.1968 | 100.2691 | 99.7316 | 4.0+63.3j | 31.2+260.9j | 114.1731 | 262.7589 | 2016-09-16
GA-72 | HM | 1-20,000 | 36.2-13.8 | 22.5+117.3j | 1.4333 | 83.7251 | 119.4384 | 4.0+63.4j | 49+298j | 99.3372 | 302.0017 | 2016-09-16
GF-71 | 138 | 1-20,000 | 138-13.8 | 4.1+77.6j | 0.9325 | 128.6865 | 77.7082 | 3.8+74.6j | 12+229.8j | 130.3707 | 230.1131 | 2016-09-16
GH-71 | 138 | 1-20,000 | 131.1-13.8 | 4.0+75.8j | 0.91087 | 131.7428 | 75.9055 | 3.7+72.9j | 11.7+224.5j | 133.4492 | 224.8047 | 2016-09-16
GH-72 | 138 | 1-20,000 | 131.1-13.8 | 3.9+74.1j | 0.89043 | 134.7662 | 74.2026 | 3.6+72.0j | 11.4+220.2j | 136.0576 | 220.4949 | 2016-09-16
GR-71 | 138 | 1-30,000 | 134.55-13.8 | 2.5+68.9j | 0.82734 | 145.0424 | 68.9453 | 2.1+67.6j | 7.1+205.4j | 145.9693 | 205.5227 | 2016-09-16
GR-72 | 138 | 1-30,00 | 134.55-13.8 | 2.3+69.6j | 0.83566 | 143.5998 | 69.638 | 1.7+67.3j | 6.3+206.5j | 145.2109 | 206.5961 | 2016-09-16
GX-72 | 138 | 1-30,000 | 134.55-13.8 | 2.3+70.8j | 0.85005 | 141.1685 | 70.8373 | 1.7+65.3j | 6.3+206.9j | 144.9304 | 206.9959 | 2016-09-16
HC-71 | 138 | 1-20,000 | 134.55-13.8 | 4.0+75.0j | 0.90128 | 133.1441 | 75.1066 | 3.8+73.1j | 11.8+223.1j | 134.2812 | 223.4118 | 2016-09-16
HC-72 | 138 | 1-20,000 | 134.55-13.8 | 4.0+71.8j | 0.86294 | 139.0601 | 71.9113 | 3.8+69.9j | 11.8+213.5j | 140.3011 | 213.8258 | 2016-09-16
HK-71 | 138 | 1-20,000 | 134.55-13.8 | 4.2+76.8j | 0.92298 | 130.0141 | 76.9148 | 3.5+74.1j | 11.9+227.7j | 131.5727 | 228.0107 | 2012-03-19
HK-72 | 138 | 1-20,000 | 138-13.2 | 4.2+81.1j | 0.9745 | 123.1395 | 81.2087 | 3.7+78.5j | 12.1+240.7j | 124.4793 | 241.0039 | 2012-03-19
HP-71 | 138 | 1-22,400 | 134.55-13.2 | 4.2+77.2j | 0.92777 | 129.3424 | 77.3142 | 3.5+74.6j | 11.9+229j | 130.8278 | 229.309 | 2021-07-13
IK-71 | 138 | 1-14,000 | 138-13.09 | 3.3+76.7j | 0.92125 | 130.2576 | 76.771 | 3.1+74.9j | 9.7+228.3j | 131.2876 | 228.506 | 2016-09-19
IL-72 | 138 | 1-20,200 | 138-13.8 | 2.9+69.4j | 0.83353 | 143.9666 | 69.4606 | 2.7+67.5j | 8.5+206.3j | 145.296 | 206.475 | 2016-03-15
IO-71 | 138 | 1-14,000 | 138-13.2 | 3.5+76.1j | 0.91417 | 131.2673 | 76.1804 | 3.3+74.0j | 10.3+226.2j | 132.4887 | 226.4344 | 2016-02-25
IO-72 | 138 | 1-14,000 | 138-13.2 | 3.6+76.4j | 0.91782 | 130.745 | 76.4848 | 3.3+74.0j | 10.5+226.8j | 132.1336 | 227.0429 | 2016-02-25
IP-71 | 138 | 1-22,400 | 138-13.2 | 3.0+72.0j | 0.86475 | 138.7685 | 72.0625 | 2.7+70.2j | 8.7+214.2j | 139.9406 | 214.3766 | 2016-07-14
IP-72 | 138 | 1-20,000 | 138-13.2 | 4.4+73.6j | 0.88478 | 135.6274 | 73.7314 | 4.2+71.8j | 13+219j | 136.7456 | 219.3855 | 2016-07-14
IW-71 | 138 | 1-20,000 | 138-13.8 | 4.0+73.2j | 0.87971 | 136.4085 | 73.3092 | 3.7+71.1j | 11.7+217.5j | 137.7319 | 217.8145 | 2016-04-04
IW-72 | 138 | 1-20,000 | 138-13.8 | 4.1+71.7j | 0.86181 | 139.2425 | 71.8171 | 3.8+69.6j | 12+213j | 140.6221 | 213.3378 | 2016-04-04
JI-71 | 138 | 1-30,000 | 138-13.8 | 2.9+64.7j | 0.77718 | 154.4045 | 64.765 | 2.6+62.8j | 8.4+192.2j | 155.9386 | 192.3835 | 2016-09-16
JL-71 | IV | 1-20,000 | 34.4+13.8 | 6.9+98.6j | 1.1861 | 101.1725 | 98.8411 | 2.2+63.9j | 16+261.1j | 114.6834 | 261.5898 | 2012-09-13
JN-71 & 72 | JD | 1-6,500 | 32.2-13.2 | 15.8+135.8j | 1.6406 | 73.1443 | 136.7161 | 12.5+122.6j | 44.1+394.2j | 75.6317 | 396.6591 | 2016-09-19
JN-71 & 72 | JD | 1-6,500 | 32.2-13.2 | 15.9+136.8j | 1.6527 | 72.6106 | 137.7209 | 12.5+123.2j | 44.3+396.8j | 75.138 | 399.2652 | 2016-09-19
JN-71 & 72 | JD | 2-6,500 | 32.2-13.2 | 8.1+71.8j | 0.86707 | 138.3979 | 72.2554 | 6.2+61.4j | 22.4+205j | 145.4756 | 206.2202 | 2016-09-19 | JN-71 & 72 are normally paralleled
JT-71 | NF | 1-10,000 | 34.4+13.8 | 17.3+100.3j | 1.2214 | 98.2501 | 101.781 | 4.0+65.9j | 38.6+266.5j | 111.4078 | 269.2809 | 2016-09-19
JT-72 | IV | 1-10,000 | 34.4+13.8 | 8.7+84.4j | 1.0182 | 117.8589 | 84.8472 | 4.1+66.1j | 21.5+234.9j | 127.1823 | 235.8819 | 2016-09-19
IO-71 | 138 | 1-11,200 | 138-13.2 | 3.5+75.6j | 0.90817 | 132.1336 | 75.681 | 4.0+77.2j | 11+228.4j | 131.1964 | 228.6647 | 2016-02-25
IO-72 | 138 | 1-11,200 | 138-13.2 | 3.5+75.9j | 0.91177 | 131.6124 | 75.9807 | 4.1+77.7j | 11.1+229.5j | 130.5663 | 229.7683 | 2016-02-25
KD-71 | 138 | 1-30,000 | 134.55-13.8 | 3.0+71.7j | 0.86115 | 139.3481 | 71.7627 | 2.3+66.8j | 8.3+210.2j | 142.6101 | 210.3638 | 2012-01-19
KD-72 | 138 | 1-30,000 | 134.55-13.8 | 3.0+71.5j | 0.85875 | 139.7372 | 71.5629 | 2.4+66.8j | 8.4+209.8j | 142.8789 | 209.9681 | 2012-01-19
KH-71 | 138 | 1-20,000 | 134.55-13.8 | 4.6+75.4j | 0.90648 | 132.3799 | 75.5402 | 3.7+69.8j | 12.9+220.6j | 135.7608 | 220.9769 | 2016-09-16
KH-72 | 138 | 1-20,000 | 134.55-13.8 | 4.6+75.0j | 0.90169 | 133.0833 | 75.1409 | 3.7+69.4j | 12.9+219.4j | 136.5008 | 219.7789 | 2016-09-16
KI-71 | 138 | 1-20,000 | 138-13.8 | 4.1+75.4j | 0.90614 | 132.4304 | 75.5114 | 3.9+73.3j | 12.1+224.1j | 133.6741 | 224.4264 | 2016-09-16
KI-72 | 138 | 1-20,000 | 138-13.8 | 4.1+72.3j | 0.86899 | 138.0907 | 72.4162 | 3.7+69.9j | 11.9+214.5j | 139.6454 | 214.8298 | 2016-09-16
KK-71 | 138 | 1-20,000 | 138-13.8 | 2.5+64.4j | 0.77338 | 155.1626 | 64.4485 | 2.3+62.4j | 7.3+191.2j | 156.7895 | 191.3393 | 2017-02-10
KL-71 | 138 | 1-30,000 | 134.55-13.8 | 3.5+68.2j | 0.81948 | 146.4349 | 68.2898 | 2.6+62.6j | 9.6+199j | 150.5787 | 199.2314 | 2017-02-10
KL-72 | 138 | 1-30,000 | 134.55-13.8 | 3.4+72.3j | 0.86856 | 138.1599 | 72.3799 | 2.5+66.6j | 9.3+211.2j | 141.9079 | 211.4047 | 2017-02-10
KN-71 | JD | 1-12,500 | 34.4-13.8 | 19.9+114.2j | 1.3911 | 86.2657 | 115.9209 | 5.9+65.2j | 45.7+293.6j | 100.9641 | 297.1354 | 2012-01-18
KN-72 | JD | 1-12,500 | 34.4-13.8 | 19.8+113.7j | 1.3849 | 86.6468 | 115.4111 | 5.4+63.8j | 45+291.2j | 101.8135 | 294.6565 | 2012-01-18
KP-71 | 138 | 1-30,000 | 138-13.8 | 2.7+70.8j | 0.85022 | 141.1403 | 70.8515 | 1.9+64.4j | 7.3+206j | 145.5397 | 206.1293 | 2017-02-10
KP-72 | 138 | 1-30,000 | 138-13.8 | 3.2+69.6j | 0.83608 | 143.5265 | 69.6735 | 2.4+63.1j | 8.8+202.3j | 148.1545 | 202.4913 | 2017-02-10
KR-71 | JD | 1-20,000 | 36.2-13.8 | 10.4+87.5j | 1.0574 | 113.4869 | 88.1159 | 4.7+68.8j | 25.5+243.8j | 122.3841 | 245.1299 | 2017-02-13
KR-72 | JD | 1-20,000 | 36.2-13.8 | 10.4+86.8j | 1.049 | 114.3892 | 87.4208 | 4.7+68.1j | 25.5+241.7j | 123.4357 | 243.0414 | 2017-02-13
KT-71 | MF | 1-37,500 | 35.3-13.8 | 26.9+131.4j | 1.6095 | 74.5572 | 134.1252 | 5.4+63.0j | 59.2+325.8j | 90.5975 | 331.1348 | 2018-09-10
KY-71 | 138 | 1-30,000 | 134.55-13.8 | 3.1+74.6j | 0.89597 | 133.9327 | 74.6644 | 2.2+67.2j | 8.4+216.4j | 138.5278 | 216.563 | 2017-02-13
KY-72 | 138 | 1-30,000 | 134.55-13.8 | 3.2+70.9j | 0.85167 | 140.9003 | 70.9722 | 2.3+63.4j | 8.7+205.2j | 146.0676 | 205.3843 | 2017-02-13
LA-71 | 138 | 1-30,000 | 138-13.8 | 3.3+72.4j | 0.8697 | 137.9783 | 72.4752 | 2.7+67.3j | 9.3+212.1j | 141.3069 | 212.3038 | 2012-08-27
LA-72 | 138 | 1-30,000 | 138-13.8 | 2.9+68.0j | 0.81674 | 146.9253 | 68.0618 | 2.2+62.9j | 8+198.9j | 150.7077 | 199.0608 | 2012-08-27
LE-71 | 138 | 1-20,000 | 134.55-13.8 | 4.4+77.3j | 0.9291 | 129.157 | 77.4251 | 3.8+73.2j | 12.6+227.8j | 131.4935 | 228.1482 | 2017-02-13
LE-72 | 138 | 1-20,000 | 134.55-13.8 | 4.5+73.0j | 0.87766 | 136.7268 | 73.1386 | 3.8+68.8j | 12.8+214.8j | 139.4175 | 215.181 | 2017-02-13
LF-72 | 138 | 1-18,000 | 138-13.8 | 2.7+66.2j | 0.79506 | 150.9319 | 66.255 | 2.3+63.5j | 7.7+195.9j | 153.0212 | 196.0513 | 2018-09-10
LI-73 | 138 | 1-20,000 | 138-13.8 | 4.1+74.9j | 0.90015 | 133.3118 | 75.0121 | 3.7+71.7j | 11.9+221.5j | 135.2451 | 221.8194 | 2017-02-13
LM-71 | 138 | 1-30,000 | 138-13.8 | 2.7+64.8j | 0.77827 | 154.1872 | 64.8562 | 2.4+62.8j | 7.8+192.4j | 155.7972 | 192.558 | 2017-02-13
LM-72 | 138 | 1-30,000 | 138-13.8 | 2.8+70.8j | 0.85026 | 141.1326 | 70.8553 | 2.4+68.1j | 8+209.7j | 142.9575 | 209.8525 | 2017-02-13
LO-71 | MF | 1-20,000 | 35.26-13.8 | 24+114.28j | 1.4013 | 85.6363 | 116.7729 | 3.4+47.5j | 51.4+276.06j | 106.836 | 280.8044 | 2017-02-20
LT-71 | MF | 1-12,500 | 34.5-13.8 | 26.2+129.4j | 1.5843 | 75.7428 | 132.0258 | 5.3+66.5j | 57.7+325.3j | 90.8052 | 330.3776 | 2017-02-20
LT-72 | MF | 1-12,500 | 34.5-13.8 | 27.2+135.0j | 1.6526 | 72.6148 | 137.7129 | 4.6+62.2j | 59+332.2j | 88.9156 | 337.3986 | 2017-02-20
MB-71 | 138 | 1-20,000 | 141.45-13.0 | 4.2+73.9j | 0.88823 | 135.1 | 74.0193 | 4.0+72.1j | 12.4+219.9j | 136.2093 | 220.2493 | 2012-01-19
MB-72 | 138 | 1-20,000 | 141.45-13.0 | 2.0+66.7j | 0.80076 | 149.8577 | 66.73 | 1.8+65.1j | 5.8+198.5j | 151.069 | 198.5847 | 2012-01-19
ME-71 | ST | 1-14,000 | 35.5-13.8 | 15.4+112.8j | 1.3662 | 87.8377 | 113.8464 | 3.7+65.1j | 34.5+290.7j | 102.48 | 292.7401 | 2017-02-15
MG-71 | MF | 1-12,500 | 35.3-13.8 | 10.1+90.2j | 1.0892 | 110.1762 | 90.7637 | 5.8+64.2j | 26+244.6j | 121.9621 | 245.978 | 2017-03-13
MK-71 | NT | 1-12,500 | 36.2-13.8 | 11.4+93.5j | 1.1303 | 106.1657 | 94.1924 | 5.3+65.4j | 28.1+252.4j | 118.1291 | 253.9594 | 2016-03-15
MK-72 | NT | 1-14,000 | 34.5-13.2 | 10.1+92.2j | 1.113 | 107.8149 | 92.7515 | 3.3+66.1j | 23.5+250.5j | 119.2369 | 251.5999 | 2016-03-15
MX-71 | 138 | 1-12,000 | 138-13.8 | 4.1+77.9j | 0.93609 | 128.1923 | 78.0078 | 3.6+74.5j | 11.8+230.3j | 130.0942 | 230.6021 | 2012-01-18
NE-71 | 138 | 1-30,000 | 141.45-13.8 | 2.7+68.3j | 0.82024 | 146.2986 | 68.3533 | 2.4+66.2j | 7.8+202.8j | 147.8197 | 202.9499 | 2017-03-13
NE-72 | 138 | 1-30,000 | 138-13.8 | 2.3+66.4j | 0.79728 | 150.5121 | 66.4398 | 2.1+64.3j | 6.7+197.1j | 152.1191 | 197.2138 | 2017-03-13
NL-71 | 138 | 1-20,000 | 134.55-13.8 | 4.8+74.1j | 0.89106 | 134.6705 | 74.2553 | 4.3+71.4j | 13.9+219.6j | 136.3392 | 220.0395 | 2017-03-13
NP-71 | 138 | 1-20,000 | 141.45-13.8 | 4.2+75.6j | 0.9086 | 132.0715 | 75.7166 | 3.8+73.0j | 12.2+224.2j | 133.6114 | 224.5317 | 2017-03-13
NS-71 | 138 | 1-20,000 | 138-13.8 | 2.4+68.2j | 0.81891 | 146.5369 | 68.2422 | 2.1+65.7j | 6.9+202.1j | 148.3549 | 202.2178 | 2017-03-14
NS-72 | 138 | 1-30,000 | 138-13.8 | 2.7+70.1j | 0.84182 | 142.5477 | 70.152 | 2.3+67.6j | 7.7+207.8j | 144.2706 | 207.9426 | 2017-03-14
NW-71 | 138 | 1-14,000 | 141.45-13.8 | 3.8+79.2j | 0.95149 | 126.1175 | 79.2911 | 3.3+75.8j | 10.9+234.2j | 127.9571 | 234.4535 | 2017-03-14
NW-72 | 138 | 1-20,000 | 141.45-13.8 | 3.8+71.8j | 0.86281 | 139.0811 | 71.9005 | 3.2+68.5j | 10.8+212.1j | 141.2597 | 212.3748 | 2017-03-14
OC-71 | NY | 1-20,000 | 34.4-13.5 | 15.1+107.1j | 1.2979 | 92.4563 | 108.1592 | 3.4+62.2j | 33.6+276.4j | 107.7452 | 278.4348 | 2012-01-18
OH-71 | NY | 1-14,000 | 35.3-13.8 | 9.3+93.8j | 1.1311 | 106.0896 | 94.2599 | 3.9+59.0j | 22.5+246.6j | 121.1513 | 247.6243 | 2012-01-18
OX-71 | MF | 1-12,500 | 36-13.2 | 27.5+123.6j | 1.5195 | 78.975 | 126.6223 | 3.2+51.7j | 58.2+298.9j | 98.5178 | 304.5135 | 2016-02-29
PG-71 | 138 | 1-20,000 | 138-13.8 | 2.7+51.0j | 0.61286 | 195.8042 | 51.0714 | 1.8+47.6j | 7.2+149.6j | 200.3029 | 149.7732 | 2017-03-14
PN-71 | 138 | 1-30,000 | 138-13.8 | 3.6+70.9j | 0.8519 | 140.8623 | 70.9913 | 2.0+64.3j | 9.2+206.1j | 145.4156 | 206.3052 | 2012-02-23
QI-71 | NY | 1-12,500 | 35.3-13.8 | 35.9+121.8j | 1.5238 | 78.7522 | 126.9805 | 5.8+63.0j | 77.6+306.6j | 94.8563 | 316.2678 | 2016-12-02
QN-71 | 138 | 1-14,000 | 138-13.2 | 3.9+80.6j | 0.96833 | 123.9245 | 80.6943 | 3.1+74.4j | 10.9+235.6j | 127.1984 | 235.852 | 2016-01-18
QZ-71 | MF | 1-14,000 | 34.4-13.8 | 30.4+150.4j | 1.8413 | 65.1714 | 153.4416 | 5.3+63.8j | 66.1+364.6j | 80.9622 | 370.5433 | 2016-02-29
RU-72 | ST | 1-20,000 | 34.4-13.8 | 18.7+101.4j | 1.2373 | 96.9839 | 103.1099 | 3.4+63.24j | 40.8+266.04j | 111.4619 | 269.1504 | 2016-03-30
SA-71 | SP | 1-12,500 | 35.3-13.8 | 17.1+115.7j | 1.4035 | 85.5016 | 116.9568 | 3.9+58.3j | 38.1+289.7j | 102.6713 | 292.1946 | 2017-03-15
SP-71 | 138 | 1-20,000 | 138-13.8 | 5.5+78.9j | 0.9491 | 126.4359 | 79.0915 | 3.8+72.6j | 14.8+230.4j | 129.9405 | 230.8749 | 2017-03-15 | Stacy Supply
UR-71 | SP | 1-12,500 | 36.2-13.8 | 43.7+155.4j | 1.9371 | 61.9473 | 161.4275 | 5.99+65.6j | 93.39+376.4j | 77.3569 | 387.8127 | 2018-09-18
VN-71 | SN | 1-12,500 | 36.2-13.8 | 14.3+96.6j | 1.1718 | 102.4037 | 97.6527 | 5.4+64.8j | 34+258j | 115.2823 | 260.2307 | 2017-03-15
WE-71 | SN | 1-5,000 | 36.2-13.8 | 23.2+164.0j | 1.9876 | 60.3745 | 165.6328 | 12.8+125.1j | 59.2+453.1j | 65.6525 | 456.951 | 2018-09-10
WF-71 | SN | 1-12,500 | 36.2-13.8 | 19.3+114.2j | 1.3898 | 86.3413 | 115.8194 | 5.6+64.9j | 44.2+293.3j | 101.1423 | 296.6117 | 2017-03-15 | 71-WE-T 6.29% @ 5 MVA no test report, used standard X/R Ratio
WF-72 | SN | 1-14,000 | 36.2-13.8 | 17.4+109.9j | 1.3352 | 89.8724 | 111.2689 | 3.7+60.6j | 38.5+280.4j | 105.9955 | 283.0308 | 2017-03-15
ZN-71 | 138 | 1-20,000 | 138-13.8 | 4.9+76.0j | 0.91389 | 131.3063 | 76.1578 | 3.8+69.2j | 13.6+221.2j | 135.3683 | 221.6177 | 2017-03-17

## 13kV Line
Positive Sequence 13.2 kV Line and Cable Impedance | [7 empty] | Zero Sequence 13.2 kV Line and Cable Impedance
Overhead | [7 empty] | Overhead
Wire Type | % Z+ Per 1000' @ 100 MVA | [6 empty] | Wire Type | % Zo Per 1000' @ 100 MVA
636 MCM ACSR | 1.6+5.6j | = | 5.8241 | Ð | 74.0546 |  | 1.2925 | 636 MCM ACSR | 6.7+18.3j | = | 19.4879 | Ð | 69.8913 | 1.2198
336 MCM ACSR | 3.1+6.0j | = | 6.7535 | Ð | 62.6761 |  | 1.0939 | 336 MCM ACSR | 9.5+20.4j | = | 22.5036 | Ð | 65.0293 | 1.135
4/0 ACSR | 4.8+6.2j | = | 7.8409 | Ð | 52.2532 |  | 0.91199 | 4/0 ACSR | 11.3+20.7j | = | 23.5835 | Ð | 61.3702 | 1.0711
1/0 Cu | 6.0+6.8j | = | 9.0686 | Ð | 48.5763 |  | 0.84782 | 1/0 Cu | 12.2+21.2j | = | 24.4598 | Ð | 60.0808 | 1.0486
1/0 - 7 Strand Al | 9.7+6.1j | = | 11.4586 | Ð | 32.1644 |  | 0.56137 | 1/0 - 7 Strand Al | 16.9+23.5j | = | 28.9458 | Ð | 54.2782 | 0.94733
#4 Cu | 15+7.4j | = | 16.726 | Ð | 26.2587 |  | 0.4583 | #4 Cu | 21.7+24.0j | = | 32.3557 | Ð | 47.8812 | 0.83568
#6 Cu | 23.8+7.7j | = | 25.0146 | Ð | 17.9279 |  | 0.3129 | #6 Cu | 30.8+26.8j | = | 40.8274 | Ð | 41.0275 | 0.71607
Cable Type | % Z+ Per 1000' @ 100 MVA | [6 empty] | Cable Type | % Zo Per 1000' @ 100 MVA
350 MCM Al 1-Conductor XLP DB | 4.4+4.0j | = | 5.9464 | Ð | 42.2737 |  | 0.73782 | 350 MCM Al 1-Conductor XLP DB | 12.2+3.6j | = | 12.7201 | Ð | 16.4404 | 0.28694
500 MCM Cu 1-Conductor XLP | 1.4+2.5j | = | 2.8653 | Ð | 60.7512 |  | 1.0603 | 500 MCM Cu 1-Conductor XLP | 5.6+1.5j | = | 5.7974 | Ð | 14.9951 | 0.26171
500 MCM Al 1-Conductor XLP DB | 3.6+3.5j | = | 5.021 | Ð | 44.1931 |  | 0.77131 | 500 MCM Al 1-Conductor XLP DB | 8.7+2.2j | = | 8.9739 | Ð | 14.1911 | 0.24768
3/0 MCM Al 1-Conductor XLP DB | 7.5+4.7j | = | 8.851 | Ð | 32.074 |  | 0.5598 | 3/0 MCM Al 1-Conductor XLP DB | 21.3+9.6j | = | 23.3634 | Ð | 24.2613 | 0.42344
#2 Al 1-conductor PE, DB | 16.8+3.2j | = | 17.102 | Ð | 10.7843 |  | 0.18822 | #2 Al 1-conductor PE, DB | 37.0+21.8j | = | 42.9446 | Ð | 30.5061 | 0.53243
600 MCM Cu 3-Conductor PILC | 1.1+1.4j | = | 1.7804 | Ð | 51.8428 | * | 0.90483 | 600 MCM Cu 3-Conductor PILC | 19.6+2.3j | = | 19.7345 | Ð | 6.6929 | 0.11681
750 MCM Al 1-Conductor XLP | 1.6+2.4j | = | 2.8844 | Ð | 56.3099 |  | 0.98279 | 750 MCM Al 1-Conductor XLP | 6.2+1.6j | = | 6.4031 | Ð | 14.4703 | 0.25255
[6 empty] | * |  | Does not include 500 MCM neutral conductor in the return path. Return path is in the sheath of the concentric neutral strands
Reactors: At Ashtabula between main busses and load busses j15.75% @ 100 MVA DB = Direct buried cable with concentric neutral strands. Resistance is increased due to proximity effect

## 11kV Bus
Positive Sequence Impedances to 11.5 kV Busses | [8 empty] | Zero Sequence Impedances to 11.5 kV Busses
11.5 kV Base Voltage | [8 empty] | 11.5 kV Base Voltage
Station | Supplied from (System) | Transformer No. - kVA | Tap Ratio | % Z @ 100MVA | D e @ 120 V | Short Circuit MVA | Short Circuit kA |  | % Zo @ 100MVA | % Z (L_G) @ 100MVA | Short Circuit MVA |  | Update
BK-1 & 3 | IV | 2-12,000 | 34.5-11.7-4.5 | 3.1+37.9j | 0.45632 | 262.974 | 13.2028 | 38.0266 | 2.4+368.0j | 8.6+443.8j | 67.5853 | 443.8833 | 2016-10-13
CK-1 & 3 | 138 | 2-36,000 | 138.6-11.5 | 0.75+20.0j | 0.24017 | 499.6488 | 25.0853 | 20.0141 | 12.1+302.1j | 13.6+342.1j | 87.6244 | 342.3702 | 2016-10-26 | Assumes 2-8 Ohm Grounding transformers (2200 A) and X/R =25
CL-1,2,3 | 138 | 3-36,000 | 138.6-11.5 | 0.59+7.93j | 0.095423 | 1257.5582 | 63.1368 | 7.9519 | 316+61.6j | 317.18+77.46j | 91.8832 | 326.5015 | 2016-12-07 | *No Gnd Xfmr and resistor info available.Used o Sequence impedance from the 1980 version of the bus impedance sheets ("Andy" sheets) Assumes 4,600A
GT-1 & 3 | 138 | 2-36,000 | 138.6-11.5 | 0.69+19.88j | 0.2387 | 502.7154 | 25.2393 | 19.892 | 17.3+406.2j | 18.68+445.96j | 67.2117 | 446.3511 | 2016-12-19 | From CAPE Assumes 1-16 Ohm Grounding transformer (1200 A) and X/R =21 and 1-8 Ohm Grounding transformer (2200 A) and X/R =25 and
HL-1,2,3 & 4 Bus 1 or A | 138 | 4-25,000 | 145.2-11.5 | 0.52+13.08j | 0.15708 | 763.9225 | 38.3534 | 13.0903 | 39.7+433.0j | 40.74+459.16j | 65.081 | 460.9638 | 2016-12-20 | Per Cape Assumes 4 -23 Ohm grounding transformers per Bus (800 A) and X/R=10.89
HL-1,2,3 & 4 Bus 2 or B | 138 | 4-25,000 | 145.2-11.5 | 0.52+13.01j | 0.15624 | 768.0263 | 38.5594 | 13.0204 | 39.7+433.0j | 40.74+459.02j | 65.1007 | 460.8244 | 2016-12-20 | Per Cape Assumes 4 -23 Ohm grounding transformers per Bus (800 A) and X/R=10.89
HM-3 & 5 Bus 1 or A | 138 | 2-36,000 | 138.6-36-11.5 | 0.86+15.24j | 0.18317 | 655.1257 | 32.8911 | 15.2642 | 38.0+710.7j | 39.72+741.18j | 40.418 | 742.2435 | 2017-01-05 | From CAPE assumes 9.5 Ohm Gnd Xfmr (2000 A)
HM-2 & 4 Bus 2 or B | 138 | 2-36,000 | 138.6-36-11.5 | 0.86+14.94j | 0.17958 | 668.2378 | 33.5494 | 14.9647 | 38.0+710.7j | 39.72+740.58j | 40.4507 | 741.6444 | 2017-01-05 | From CAPE assumes 9.5 Ohm Gnd Xfmr (2000 A)
HO-1 & 2 | 138 | 2-42,000 | 138-11.5 | 0.58+16.98j | 0.20388 | 588.5849 | 29.5504 | 16.9899 | 39.7+432.9j | 40.86+466.86j | 64.0144 | 468.6446 | 2016-10-13
JY-1, 2 & 4 | JD | 3-10,000 | 36-12-4.6 | 2.8+35.5j | 0.42732 | 280.818 | 14.0987 | 35.6103 | 2.2+708.0j | 7.8+779j | 38.509 | 779.039 | 2016-12-19 | Note: Jersey Sub currently operating with 1 Reactor
LS-6,7 & 8 X or 600 Bus | 138 | 3-50,000 | 132-11.5 | 0.36+13.25j | 0.15906 | 754.4386 | 37.8772 | 13.2549 | 19.66+412.88j | 20.38+439.38j | 68.2047 | 439.8524 | 2016-11-02 | Assumes 3-16 Ohm Grounding transformers (1200 A) and X/R =21
LS-6,7 & 8 Y or 900 Bus | 138 | 3-50,000 | 132-11.5 | 0.4+13.6j | 0.16327 | 734.9763 | 36.9001 | 13.6059 | 19.66+412.88j | 20.46+440.08j | 68.0959 | 440.5554 | 2016-11-02 | Assumes 3-16 Ohm Grounding transformers (1200 A) and X/R =21
NB-1,2,3 & 4 | 69 | 4-27,000 | 69.3-11.5 | 0.75+13.36j | 0.16057 | 747.3263 | 37.5201 | 13.381 | 9.15+378.0j | 10.65+404.72j | 74.0997 | 404.8601 | 2016-12-30 | *No Gnd Xfmr info available.Used o Sequence impedance from the 1980 version of the bus impedance sheets ("Andy" sheets) Assumes 3,700A
0

## 11kV Line
Positive Sequence 11.5 kV Line and Cable Impedance | [6 empty] | Zero Sequence 11.5 kV Line and Cable Impedance
Overhead | [6 empty] | Overhead
Wire Type | % Z+ Per Mile' @ 100 MVA | [5 empty] | Wire Type | % Zo Per Mile' @ 100 MVA
477 MCM ACSR | 14.8+42.1j | = | 44.6257 | Ð | 70.6312 | 1.2327 | 477 MCM ACSR | 29.6+198.0j | = | 200.2003 | Ð | 81.4975 | 1.4224
4/0 ACSR | 37.8+50.1j | = | 62.7603 | Ð | 52.9658 | 0.92443 | 4/0 ACSR | 39.6+203.4j | = | 207.219 | Ð | 78.9829 | 1.3785
4/0 Cu | 21.0+45.5j | = | 50.1124 | Ð | 65.2249 | 1.1384 | 4/0 Cu | 33.0+200.3j | = | 203.0002 | Ð | 80.6444 | 1.4075
1/0 Cu | 41.9+49.7j | = | 65.0054 | Ð | 49.8672 | 0.87035 | 1/0 Cu | 44.5+201.9j | = | 206.7459 | Ð | 77.5704 | 1.3539
#2 Cu | 104.0+54.5j | = | 117.4149 | Ð | 27.6563 | 0.48269 | #2 Cu | 78.4+204.3j | = | 218.8265 | Ð | 69.0057 | 1.2044
#DIV/0!
NOTE: Overhead line impedance values are for a 24" flat spacing configuration
Cable Type | % Z+ Per 1000' @ 100 MVA | [5 empty] | Cable Type | % Zo Per 1000' @ 100 MVA
600 MCM Cu | 1.63+2.02j | = | 2.5956 | Ð | 51.0989 | 0.89184 | 600 MCM Cu | 19.85+2.99j | = | 20.0739 | Ð | 8.566 | 0.14951
4/0 Cu belted | 4.44+2.49j | = | 5.0906 | Ð | 29.2842 | 0.51111 | 4/0 Cu belted | 27.7+3.71j | = | 27.9473 | Ð | 7.6285 | 0.13314
# 2 Leaded | 14.5+3.1j | = | 14.8277 | Ð | 12.0678 | 0.21062 | # 2 Leaded | 0+0j | = | 0 | Ð | #DIV/0! | #DIV/0!
#DIV/0!
#DIV/0!
Reactors | % Z+ @ 100 MVA |  |  |  |  | #REF!
600MCM Cu (400A) | 0+37.8j |  |  |  |  | #DIV/0!
2-600 MCM Cu (800A) | 0+17.2j |  |  |  |  | #DIV/0!
4/0 Cu (200A) | 0+75.6j |  |  |  |  | #REF!
HL | 0+28.2j
All 11.5 kV subtransmission feeders supplied from CK, CL, GT & NB Except V-3, 5, 19 & 21-CK have 600 MCM or 2-600 MCM or 4/0 reactors. There are no reactors at BK, and HM. HL, LS and HO reactors are j28% except on the network cables (v-203, 208, 214, 221 and 231-HO) where there are no reactors

## 4kV Bus
Positive Sequence Impedances to 4.6 kV Busses | [8 empty] | Zero Sequence Impedances to 4.6 kV Busses
4.6 kV Base Voltage | [8 empty] | 4.6 kV Base Voltage
Station | Supplied from (System) | Transformer No. - kVA | Tap Ratio | % Z @ 100MVA | D e @ 120 V | Short Circuit MVA | Short Circuit kA |  | % Zo @ 100MVA | % Z (L_G) @ 100MVA | Short Circuit MVA |  | Update
AL-41 | NF | 1-6,667 | 36.0-4.6 | 22.6+130.4j | 1.5881 | 75.5607 | 9.484 | 132.3439 |  |  |  | 0 | 2017-04-12 | *
AL-42 | NF | 1-6,667 | 36.0-4.6 | 22.6+130.3j | 1.5869 | 75.617 | 9.491 | 132.2454 |  |  |  | 0 | 2017-04-12 | *
AL-43 | NF | 1-6,667 | 36.0-4.6 | 22.3+131.9j | 1.6053 | 74.7542 | 9.3827 | 133.7718 |  |  |  | 0 | 2017-04-12 | *
BB-41 & 42 (N) | LY | 2-6,667 | 36.0-4.4 | 7.1+57.4j | 0.69405 | 172.8984 | 21.7013 | 57.8374 |  |  |  | 0 | 2018-08-21 | *
BB-43 & 44 (S) | LY | 2-6,667 | 36.0-4.4 | 7.1+57.4j | 0.69405 | 172.8984 | 21.7013 | 57.8374 |  |  |  | 0 | 2018-08-21 | *
BD-45 | SN | 1-15,000 | 35.5-4.8 | 8.3+78.9j | 0.95202 | 126.0472 | 15.8208 | 79.3354 |  |  |  | 0 | 2012-05-01 | *
BD-46 | SN | 1-15,000 | 35.5-4.8 | 8.2+78.1j | 0.94235 | 127.341 | 15.9832 | 78.5293 |  |  |  | 0 | 2012-05-01 | *
BF-41 & 42 | NF | 2-3,000 | 34.5-4.4 | 12.9+82.3j | 0.99966 | 120.041 | 15.0669 | 83.3049 |  |  |  | 0 | 2017-10-27 | *
BK-1 &3 | IV | 2-12,000 | 34.5-11.7-4.5 | 3.1+38.0j | 0.45751 | 262.2866 | 32.9208 | 38.1262 |  |  |  | 0 | 2017-01-07 | *
BL-41 & 42 | HM | 2-3,000 | 34.5-4.4 | 18.1+100.9j | 1.2301 | 97.5509 | 12.2441 | 102.5106 |  |  |  | 0 | 2017-10-30 | *
BR-41 & 42 | AN | 2-3,000 | 37.6-4.8 | 18.0+121.3j | 1.4715 | 81.5473 | 10.2354 | 122.6283 |  |  |  | 0 | 2017-10-30 | *
BT-41 | ST | 1-5,000 | 34.2-4.8 | 26.9+182.1j | 2.2089 | 54.3254 | 6.8186 | 184.0761 |  |  |  | 0 | 2017-10-30 | *
BU-41 & 42 | JD | 1-5,000 | 36.2-4.8 | 21.4+157.9j | 1.9121 | 62.7575 | 7.877 | 159.3436 |  |  |  | 0 | 2017-10-30 | *
CC-41 | NY | 1-5,000 | 32.778-4.6 | 33.3+183.5j | 2.238 | 53.6202 | 6.7301 | 186.497 |  |  |  | 0 | 2017-10-30 | *
CD-41 | MF | 1-3,000 | 32.775-4.6 | 46.6+208.7j | 2.5661 | 46.7641 | 5.8696 | 213.8393 |  |  |  | 0 | 2017-10-30 | *
CD-42 | MF | 1-3,000 | 32.775-4.6 | 49.2+208.6j | 2.5719 | 46.6584 | 5.8563 | 214.3236 |  |  |  | 0 | 2017-10-30 | *
CG-41 & 42 | CK | 2-6,250 | 11.7-4.8 | 14.9+109.0j | 1.3202 | 90.8978 | 11.409 | 110.0137 |  |  |  | 0 | 2018-07-30 | *
CN-41 & 42 | HO | 2-5,000 | 12-4.8 | 6.6+86.6j | 1.0422 | 115.1395 | 14.4517 | 86.8511 |  |  |  | 0 | 2017-10-30 | *
CR-41, 42, 43, & 44 | DS | 4-6,250 | 36.2-4.8 | 6.4+45.4j | 0.55019 | 218.1078 | 27.3757 | 45.8489 |  |  |  | 0 | 2017-10-30 | *
CT-41 & 42 (N) | LS | 2-6,250 | 12.3-4.8 | 20.2+103.2j | 1.2619 | 95.0947 | 11.9358 | 105.1584 |  |  |  | 0 | 2017-05-26 | *
CT-43 & 44 (S) | LS | 2-6,250 | 12.3-4.8 | 20.1+100.4j | 1.2287 | 97.6637 | 12.2582 | 102.3922 |  |  |  | 0 | 2017-05-26 | *
DH-41 & 42 | IV | 2-5,748 | 37.8-4.8 34.5-4.4 | 11.6+89.3j | 1.0806 | 111.0491 | 13.9383 | 90.0503 |  |  |  | 0 | 2017-05-31 | *
DO-41 | AN | 1-6,250 | 36.2-4.8 | 37.7+110.7j | 1.4033 | 85.5114 | 10.7329 | 116.9435 |  |  |  | 0 | 2016-08-08 | *
DV-41 | CL | 1-3,000 | 11.431-4.6 | 137.9+251.1j | 3.4377 | 34.9071 | 4.3814 | 286.4745 |  |  |  | 0 | 2016-12-16 | *
DV-42 | CL | 1-3,000 | 11.431-4.6 | 127.3+237.9j | 3.2378 | 37.062 | 4.6518 | 269.8179 |  |  |  | 0 | 2016-12-16 | *
DV-43 | CL | 1-3,000 | 11.431-4.6 | 140.2+251.5j | 3.4553 | 34.7297 | 4.3591 | 287.938 |  |  |  | 0 | 2016-12-16 | *
EG-41 | NY | 1-5,000 | 36-4.43 | 36.6+187.9j | 2.2972 | 52.238 | 6.5566 | 191.4314 |  |  |  | 0 | 2017-03-31 | 6.1%Z per xfmr database, No test report. Used 10.5 X/R
FL-41 | HM | 1-2,500 | 36.2-4.8 | 39.3+286.2j | 3.4666 | 34.6158 | 4.3448 | 288.8857 |  |  |  | 0 | 2017-11-01 | *
FM-41 & 42 | GW | 2-12,500 | 36.2-4.8 | 5.4+49.9j | 0.6023 | 199.2376 | 25.0072 | 50.1913 |  |  |  | 0 | 2017-11-01 | *
FP-41 | NY | 1-6,250 | 33.5-4.8 | 19.4+153.1j | 1.8519 | 64.7986 | 8.1332 | 154.3242 |  |  |  | 0 | 2017-11-01 | *
FR-41 | JD | 1-6,667 | 36.0-4.4 | 18.6+140.8j | 1.7043 | 70.411 | 8.8376 | 142.0232 |  |  |  | 0 | 2017-02-22 | *
FR-42 | JD | 1-6,667 | 36.0-4.4 | 19.8+145.5j | 1.7621 | 68.1009 | 8.5477 | 146.841 |  |  |  | 0 | 2017-02-22 | *
FR-43 | JD | 1-6,667 | 36.0-4.4 | 17.7+140.5j | 1.6993 | 70.6162 | 8.8634 | 141.6105 |  |  |  | 0 | 2017-02-22 | *
FT-44 | GW | 1-12,500 | 36.2-4.8 | 12.9+97.2j | 1.1766 | 101.9864 | 12.8008 | 98.0523 |  |  |  | 0 | 2017-11-01 | *
GA-41 | HM | 1-6,250 | 36.2-4.8 | 24.3+167.8j | 2.0346 | 58.9795 | 7.4028 | 169.5504 |  |  |  | 0 | 2016-09-16 | *
GI-41, 42 &43 | CL | 3-6,667 | 11.717-4.6 | 7.8+56.6j | 0.68562 | 175.0243 | 21.9681 | 57.1349 |  |  |  | 0 | 2016-12-15 | 1980 Andy Sheets 17.0+103.7j. Could not find any info to explain the discrepancy
GM-41 | GW | 1-6,250 | 36.2-4.8 | 23.2+154.7j | 1.8772 | 63.9264 | 8.0237 | 156.43 |  |  |  | 0 | 2017-11-01 | *
GN-41 & 42 | SN | 2-3,000 | 36.2-4.8 | 37.9+167.2j | 2.0573 | 58.3289 | 7.3211 | 171.4417 |  |  |  | 0 | 2017-11-01 | *
GS-41 & 42 | GW | 2-12,500 | 36.2-4.8 | 4.0+44.5j | 0.53615 | 223.8167 | 28.0923 | 44.6794 |  |  |  | 0 | 2017-11-01 | *
HA-41, 42 & 43 | LY | 3-6,250 | 36.2-4.8 | 6.0+52.6j | 0.63529 | 188.8892 | 23.7083 | 52.9411 |  |  |  | 0 | 2017-11-01 | *
HB-41 | ST | 1-3,000 | 34.2-4.8 | 24.2+212.1j | 2.5617 | 46.8436 | 5.8796 | 213.4761 |  |  |  | 0 | 2017-11-01 | *
HH-41 | MF | 1-3,000 | 37.6-4.8 | 30.2+226.7j | 2.7444 | 43.7249 | 5.4881 | 228.7027 |  |  |  | 0 |  | No xfmr data available
HN-41 | MF | 1-2,000 | 31.050-4.6 | 94.7+424.4j | 5.218 | 22.9971 | 2.8865 | 434.8373 |  |  |  | 0 |  | No xfmr data available
HR-41 | CL | 1-6,667 | 11.431-4.6 | 42.0+182.7j | 2.2496 | 53.3432 | 6.6953 | 187.4654 |  |  |  | 0 | 2016-12-16 | *
HR-42 | CL | 1-6,667 | 11.431-4.6 | 41.8+183.7j | 2.2607 | 53.0798 | 6.6623 | 188.3957 |  |  |  | 0 | 2016-12-16 | *
HR-43 | CL | 1-6,667 | 11.431-4.6 | 41.9+184.5j | 2.2704 | 52.8547 | 6.634 | 189.1979 |  |  |  | 0 | 2016-12-16 | * | needs updated because all 3 banks are operated in parallel now
HV-41, 42 & 43 | GT | 3-3,000 | 11.431-4.6 | 15.4+74.1j | 0.9082 | 132.1295 | 16.5842 | 75.6834 |  |  |  | 0 | 2017-11-01 | *
IA-41 & 42 | IV | 2-6,250 | 36.2-4.8 | 10.5+77.4j | 0.93731 | 128.0263 | 16.0692 | 78.109 |  |  |  | 0 | 2017-11-01 | *
IA-43 & 44 | IV | 2-6,250 | 36.2-4.8 | 9.7+78.1j | 0.9444 | 127.0647 | 15.9485 | 78.7001 |  |  |  | 0 | 2017-11-01 | *
IB-43 & 44 (E) | LS | 2-6,250 | 12.3-4.8 | 17.2+89.4j | 1.0925 | 109.8424 | 13.7868 | 91.0396 |  |  |  | 0 | 2017-11-01 | *
IB-41 & 42 (W) | LS | 2-6,250 | 12.3-4.8 | 16.1+87.6j | 1.0688 | 112.2747 | 14.0921 | 89.0672 |  |  |  | 0 | 2017-11-01 | *
ID-41 & 42 | IV | 2-6,250 | 36.2-4.8 | 13.8+100.5j | 1.2173 | 98.5775 | 12.3729 | 101.443 |  |  |  | 0 | 2017-11-08 | *
IG-41 & 42 | JD | 2-12,500 | 36.2-4.8 | 3.4+43.4j | 0.5224 | 229.7109 | 28.8321 | 43.533 |  |  |  | 0 | 2017-11-08 | *
IH-41 | JD | 1-9,375 | 36.2-4.8 | 13.2+118.2j | 1.4272 | 84.0797 | 10.5532 | 118.9348 |  |  |  | 0 | 2017-11-08 | *
IR-41 | IV | 1-6,250 | 36.2-4.8 | 15.4+144.5j | 1.7438 | 68.8145 | 8.6372 | 145.3183 |  |  |  | 0 | 2017-11-08 | *
IT-44 & 46 (W) | NB | 2-6,250 | 12.0-4.8 | 6.7+82.4j | 0.99206 | 120.96 | 15.1823 | 82.6719 |  |  |  | 0 | 2017-11-08 | *
IT-42 & 43 (E) | NB | 2-6,250 | 12.0-4.8 | 6.6+84.0j | 1.0111 | 118.6818 | 14.8963 | 84.2589 |  |  |  | 0 | 2017-11-08 | *
JA-41 & 42 | JD | 2-6,250 | 36.2-4.8 | 9.5+78.4j | 0.94768 | 126.6248 | 15.8933 | 78.9735 |  |  |  | 0 | 2017-11-08 | *
JA-43 | JD | 1-6,250 | 36.2-4.8 | 16.2+134.2j | 1.6221 | 73.9786 | 9.2854 | 135.1743 |  |  |  | 0 | 2017-11-08 | *
JP-41,42 & 43 | LY | 3-6,250 | 36.2-4.8 | 9.6+63.9j | 0.77541 | 154.7578 | 19.4244 | 64.6171 |  |  |  | 0 | 2017-11-08 | *
JS-41 & 42 | ZN | 2-5,000 | 32.775-4.6 | 13.4+101.3j | 1.2262 | 97.8642 | 12.2834 | 102.1824 |  |  |  | 0 | 2018-08-16 | *
JV-41 | JD | 1-9,375 | 36.2-4.8 | 14.1+103.7j | 1.2559 | 95.5528 | 11.9933 | 104.6542 |  |  |  |  | 2018-08-06
JV-42 | JD | 1-9,375 | 36.2-4.8 | 14.2+102.2j | 1.2382 | 96.9163 | 12.1644 | 103.1818 |  |  |  | 0 | 2018-08-06 | *
JY-1, 2 & 4 | JD | 3-10,000 | 36-12-4.6 | 3.1+48.7j | 0.58558 | 204.9241 | 25.721 | 48.7986 |  |  |  |  | 2016-03-02 | *
KA-41 | NF | 1-5,000 | 35.1-4.8 | 22.2+150.9j | 1.8303 | 65.5633 | 8.2292 | 152.5243 |  |  |  | 0 | 2017-11-10 | *
KB-41 & 42 | DS | 2-5,000 | 37.8-4.8 | 6.9+67.8j | 0.8178 | 146.7347 | 18.4173 | 68.1502 |  |  |  | 0 | 2017-11-10 | *
KM-41, 43, 44 & 45 | NB | 3-6,667 1-6,250 | 11.431-4.6 11.91-4.8 | 14.9+48.7j | 0.61114 | 196.3542 | 24.6453 | 50.9284 |  |  |  | 0 | 2017-11-16 | *
KO-41 & 42 | GT | 2-6,250 | 34.4-4.8 | 13.0+99.0j | 1.1982 | 100.1503 | 12.5703 | 99.8499 |  |  |  | 0 | 2017-11-16 | *
KV-41 | SN | 1-5,000 | 34.4-4.8 | 31.4+181.7j | 2.2127 | 54.2319 | 6.8069 | 184.3932 |  |  |  | 0 | 2017-11-16 | *
LD-41, 42 & 46 | CL | 3-3,000 | 11.05-4.6 | 52.6+87.5j | 1.2251 | 97.9498 | 12.2941 | 102.0931 |  |  |  | 0 | 2016-12-08
LD-44, 45 & 43 | CL | 3-3,000 | 11.05-4.6 | 52.6+86.3j | 1.2128 | 98.9447 | 12.419 | 101.0666 |  |  |  | 0 | 2016-12-08 | No impedance values available for 41,43,44 and 46 Transformers
LD-41, 42, 43, 44, 45 & 46 | CL | 6-3,000 | 11.05-4.6 | 26.9+51.4j | 0.69616 | 172.3736 | 21.6354 | 58.0135 |  |  |  |  | 2016-12-08 | Used 42 Transformer Impedance
LK-41 & 42 | AN | 2-3,450 | 36.0-4.6 | 9.5+75.5j | 0.91314 | 131.4141 | 16.4944 | 76.0953 |  |  |  | 0 | 2017-11-16 | No X/R ratio for 41-T available. Used 9.11
LN-41, 42 & 43 | MF | 3-6,250 | 36.2-4.8 | 9.4+68.5j | 0.8297 | 144.63 | 18.1532 | 69.142 |  |  |  | 0 | 2017-11-16 | *
LW-41 (NE) & (SE) Bus | GW | 1-22,400 | 34.5-4.8 | 7.4+104.6j | 1.2583 | 95.3639 | 11.9696 | 104.8614 |  |  |  | 0 | 2015-08-31 | *
LW-42 (NW) & (SW) Bus | GW | 1-22,400 | 34.5-4.8 | 7.4+106.5j | 1.2811 | 93.6709 | 11.7571 | 106.7568 |  |  |  | 0 | 2015-08-31 | *
LZ-41 | LY | 1-11,200 | 36-4.6 | 5.1+69.0j | 0.83026 | 144.5333 | 18.141 | 69.1882 |  |  |  |  | 2016-02-03 | *
MA-41, 42 & 43 | HM | 3-6,250 | 36.2-4.8 | 8.5+60.4j | 0.73194 | 163.9474 | 20.5778 | 60.9952 |  |  |  | 0 | 2017-12-01 | *
MD-41 | ST | 1-5,000 | 31.05-4.6 | 30.7+201.3j | 2.4435 | 49.1093 | 6.1639 | 203.6276 |  |  |  | 0 | 2016-03-30 | *
MD-42 | ST | 1-5,000 | 31.05-4.6 | 28.9+185.8j | 2.2564 | 53.1818 | 6.6751 | 188.0342 |  |  |  | 0 | 2016-03-30 | *
MH-41, 42 & 43 | GW | 3-6,250 | 36.2-4.8 | 8.9+63.4j | 0.76826 | 156.1972 | 19.605 | 64.0216 |  |  |  | 0 | 2017-11-16 | No test reports for 41 & 42. used %Z from database and X/R from 43
NM-41 | NY | 1-3,125 | 34.4-4.8 | 41.7+296.6j | 3.5942 | 33.3871 | 4.1906 | 299.517 |  |  |  | 0 | 2017-12-01 | *
NO-41 & 42 | DS | 2-5,000 | 37.8-4.8 37.6-4.8 | 13.7+83.1j | 1.0107 | 118.7342 | 14.9029 | 84.2217 |  |  |  | 0 | 2017-12-01 | *
NO-43 | DS | 1-5,000 | 37.8-4.8 | 27.1+155.6j | 1.8953 | 63.3143 | 7.9469 | 157.9423 |  |  |  | 0 | 2017-12-01 | *
NU-41 | MF | 1-3,125 | 36.2-4.8 | 48.1+315.4j | 3.8286 | 31.3434 | 3.9341 | 319.0467 |  |  |  | 0 | 2017-12-01 | *
PA-41, 42, 43 & 44 | LS | 4-6,667 | 11.717-4.6 | 10.9+60.6j | 0.73887 | 162.4102 | 20.3849 | 61.5725 |  |  |  | 0 | 2016-04-17 | *
PE-41, 42 & 43 | HM | 3-6,250 | 36.2+4.8 | 6.5+54.3j | 0.65625 | 182.8566 | 22.9512 | 54.6877 |  |  |  | 0 | 2017-12-01 | *
PK-41 | NY | 1-3,000 | 34.5+4.6 | 32.4+173.7j | 2.1204 | 56.5944 | 7.1034 | 176.6959 |  |  |  | 0 | 2017-12-01 | *
PU-41, 42 & 43 | GW | 3-6,250 | 36.2-4.8 | 6.3+59.2j | 0.71441 | 167.9705 | 21.0827 | 59.5343 |  |  |  | 0 | 2017-12-05
QK-42 | MF | 1-3,125 | 34.4-4.8 | 43.9+285.5j | 3.4663 | 34.6194 | 4.3452 | 288.8554 |  |  |  | 0 | 2017-12-05
RC-41 | SN | 1-3,000 | 31.05-4.4 | 45.3+233.9j | 2.859 | 41.9734 | 5.2683 | 238.2463 |  |  |  | 0 | 2017-12-05
RD-42 & 44 (W) | HM | 2-6,667 | 11.717-4.6 | 22.5+85.8j | 1.0644 | 112.7381 | 14.1503 | 88.7011 |  |  |  | 0 | 2017-12-05
RD-41 & 43 (E) | HM | 2-6,667 | 11.717-4.6 | 22.0+83.8j | 1.0397 | 115.4205 | 14.487 | 86.6397 |  |  |  | 0 | 2017-12-05
RK-41 | NF | 1-6,250 | 36.2-4.8 | 20.9+153.3j | 1.8566 | 64.6337 | 8.1125 | 154.7181 |  |  |  | 0 | 2017-12-05
RM-41 | ST | 1-2,000 | 32.775-4.6 | 38.3+208.7j | 2.5462 | 47.1286 | 5.9153 | 212.1852 |  |  |  | 0 | 2016-03-30
RV-41 | NY | 1-2,000 | 32.775-4.6 | 49.5+334.2j | 4.0542 | 29.5993 | 3.7151 | 337.846 |  |  |  | 0 | 2017-12-05
RW-41 | ST | 1-5,000 | 32.775-4.6 | 30.9+181.6j | 2.2105 | 54.2858 | 6.8137 | 184.2101 |  |  |  | 0 | 2016-03-30
SC-41 & 43 (S) | LS | 2-6,250 | 12.3-4.8 | 11.8+90.0j | 1.0892 | 110.1682 | 13.8277 | 90.7703 |  |  |  | 0 | 2017-12-05
SC-43 & 44 (N) | LS | 2-6,250 | 12.3-4.8 | 11.8+86.0j | 1.0417 | 115.1997 | 14.4592 | 86.8058 |  |  |  | 0 | 2017-12-05
SH-41 & 43 (N) | NF | 2-6,667 | 36.0-4.6 | 12.1+67.6j | 0.82409 | 145.6147 | 18.2768 | 68.6744 |  |  |  | 0 | 2012-01-30
SH-42 & 44 (S) | NF | 1-6,667 1-6,250 | 36.0-4.6 37.6-4.8 | 12.2+68.6j | 0.83612 | 143.5206 | 18.0139 | 69.6764 |  |  |  | 0 | 2012-01-30
SO-41, 42 & 43 | IV | 3-6,250 | 36.2-4.8 | 8.5+59.9j | 0.726 | 165.289 | 20.7462 | 60.5001 |  |  |  | 0 | 2017-12-05
TS-41 | SP | 1-3,000 | 32.775+4.6 | 35.5+179.4j | 2.1945 | 54.6811 | 6.8633 | 182.8787 |  |  |  | 0 | 2017-12-05 | was fed by NY sub now fed by SP sub
WB-41 | SN | 1-6,250 | 36.2+4.8 | 26.7+170.5j | 2.0709 | 57.9448 | 7.2729 | 172.5779 |  |  |  | 0 | 2017-12-05
WD-41 | JD | 1-6,250 | 36.2+4.8 | 24.0+146.1j | 1.7767 | 67.541 | 8.4774 | 148.0581 |  |  |  | 0 | 2017-12-05 | was fed by NF sub now fed by JD sub
WD-43 | JD | 1-6,250 | 36.2-4.8 | 23.9+149.2j | 1.8132 | 66.1804 | 8.3066 | 151.1021 |  |  |  | 0 | 2017-12-05 | was fed by NF sub now fed by JD sub
WD-44 | IV | 1-6,250 | 36.2-4.8 | 14.8+128.6j | 1.5534 | 77.2506 | 9.6961 | 129.4488 |  |  |  | 0 | 2017-12-05
WH-41 | MF | 1-6,250 | 36.2-4.8 | 27.5+171.0j | 2.0784 | 57.7377 | 7.2469 | 173.1971 |  |  |  | 0 | 2017-12-05
WH-42 | NF | 1-6,250 | 36.2-4.8 | 42.7+173.2j | 2.1406 | 56.0582 | 7.0361 | 178.3859 |  |  |  | 0 | 2017-12-05
WI-41 | ST | 1-2,000 | 11.431-4.6 | 52.2+354.2j | 4.2963 | 27.9309 | 3.5057 | 358.0258 |  |  |  | 0 | 2016-03-30
WK-41, 42 & 43 | LS | 3-6,667 | 11.431-4.6 | 9.8+63.8j | 0.77458 | 154.9228 | 19.4451 | 64.5483 |  |  |  | 0 | 2017-12-05
WL-44, 46 & 48 | NB | 3-3,000 | 11.431-4.6 | 23.6+82.3j | 1.0274 | 116.7994 | 14.66 | 85.6169 |  |  |  | 0 | 2017-10-30
WN-41,43 & 44 | GT | 3-3,000 | 11.431-4.6 | 25.8+81.4j | 1.0247 | 117.1085 | 14.6988 | 85.3909 |  |  |  |  | 2017-12-05 | No test reports for 41 & 43. used %Z and X/R from 44
WS-41 & 42 (W) | LS | 2-6,250 | 12.0-4.8 | 30.6+95.4j | 1.2022 | 99.8129 | 12.528 | 100.1874 |  |  |  |  | 2011-10-10
WS-43 & 44 (E) | LS | 2-6,250 | 12.0-4.8 | 32.0+97.8j | 1.2348 | 97.1798 | 12.1975 | 102.9021 |  |  |  |  | 2011-10-10
WT-42 & 44 (NE) | CK | 2-3,000 | 11.431-4.6 | 26.0+122.5j | 1.5027 | 79.8538 | 10.0228 | 125.2288 |  |  |  |  | 2016-10-31
WT-41 & 43 (NW) | CK | 2-3,000 | 11.431-4.6 | 26.0+122.5j | 1.5027 | 79.8538 | 10.0228 | 125.2288 |  |  |  |  | 2016-10-31
WT-46 & 47 (SW) | CK | 2-3,000 | 11.431-4.6 | 26.0+122.5j | 1.5027 | 79.8538 | 10.0228 | 125.2288 |  |  |  |  | 2016-10-31

## 4kV Line
Positive Sequence 4.6 kV Line and Cable Impedance
Overhead
Wire Type | % Z+ Per 1000' @ 100 MVA
636 MCM ACSR | 13.2+46.4j | = | 48.2411 | Ð | 74.1199 | 1.2936
336 MCM ACSR | 24.6+46.4j | = | 52.5178 | Ð | 62.0687 | 1.0833
4/0 Al | 38.8+49.7j | = | 63.0518 | Ð | 52.0214 | 0.90794
1/0 - Al | 77.6+53.5j | = | 94.255 | Ð | 34.5837 | 0.6036
1/0 - Cu | 49.7+53.5j | = | 73.0229 | Ð | 47.1088 | 0.8222
#2 - Cu | 77.6+56.3j | = | 95.8721 | Ð | 35.9615 | 0.62765
#4 - Cu | 123.0+61.5j | = | 137.5182 | Ð | 26.5651 | 0.46365
#6 - Cu | 195.8+62.0j | = | 205.3817 | Ð | 17.5704 | 0.30666
Cable Type | % Z+ Per 1000' @ 100 MVA
600 MCM Cu | 8.8+11.8j | = | 14.7201 | Ð | 53.2858 | 0.93001
350 MCM Cu | 14.8+12.4j | = | 19.308 | Ð | 39.9575 | 0.69739
4/0 Cu | 24.1+14.3j | = | 28.0232 | Ð | 30.6832 | 0.53552
1/0 Cu | 48.3+16.1j | = | 50.9127 | Ð | 18.4349 | 0.32175
# 6 Cu | 194.0+20.4j | = | 195.0696 | Ð | 6.0029 | 0.10477
# 2 ALJCN | 151.2+28.8j | = | 153.9184 | Ð | 10.7843 | 0.18822

## Shopping Center Bus
Positive Sequence Impedances to Busses | [7 empty] | Zero Sequence Impedances to Busses
Station | Supplied from (System) | Transformer No. - kVA | Tap Ratio | % Z @ 100MVA | D e @ 120 V | Short Circuit MVA |  | % Zo @ 100MVA | % Z (L_G) @ 100MVA | Short Circuit MVA |  | Update
MSC (4 kV) | HM | 1-5,000 | 37.6-4.8 | 21.6+163.4j | 1.9779 | 60.6717 | 164.8215 | 0+0j | 43.2+326.8j | 91.0076 | 329.643
GLM (13.2) | NT | 2-5,000 |  | 10.1+121.4j | 1.4618 | 82.0887 | 121.8194 |  |  |  | 0
AVD (13.2) | NT | 1-7,500 | 34.4-13.2 | 19.1+110.34j | 1.3438 | 89.3009 | 111.9809 | 5.71+79.93j | 43.91+300.61j | 98.7492 | 303.8
0
0
0
0
0
0
0
0
0
0
0
0
0